APC Smart-UPS 3000VA — LCD Panel and Battery Status Indicator Guide

KB004    Category: Infrastructure    31 views

[Applies to: BlueStar Airlines, Inc. — IT Infrastructure Team and Facilities]

Summary

This article explains the LCD display screens, LED indicators, and audible alarm patterns on APC Smart-UPS 3000VA (SUA3000RM2U) units protecting BlueStar Airlines server rooms and network closets at all hub and spoke stations. Use this guide to assess UPS health, interpret battery state, and determine whether a unit requires immediate service.

Details

Overview

The APC Smart-UPS 3000VA has a front-panel LCD that cycles through status screens and three indicator LEDs (Online, On Battery, Replace Battery). Under normal operation the unit runs in Online mode: AC input powers connected equipment and simultaneously charges the battery. Healthy baseline: Online LED solid green, LCD showing "Online – Utility OK," battery charge ≥ 80 %.

Front-Panel LED Indicators

| LED | Color / State | Meaning |
| --- | --- | --- |
| Online | Solid green | UPS is powered by utility AC and charging the battery normally. |
| Online | Off | UPS is not receiving utility AC — check the power feed and circuit breaker. |
| On Battery | Solid amber | Utility power has failed; UPS is discharging the battery to power connected equipment. |
| On Battery | Blinking amber (fast) | Battery is critically low (< 2 min estimated runtime) — initiate graceful shutdown immediately. |
| Replace Battery | Solid red | Battery has failed the self-test or is below serviceable capacity — replace within 2 business days. |
| Replace Battery | Blinking red | Battery has completely failed — equipment is unprotected; replace immediately. |

LCD Status Screens

| Screen Display | Meaning | Action |
| --- | --- | --- |
| Online – Utility OK | Normal operation; utility power healthy. | No action required. |
| On Battery – Utility Failure | Utility power lost; running on battery. | Investigate power failure; prepare for graceful shutdown. |
| Replace Battery | Battery self-test failed or capacity < 25 %. | Order replacement battery (APCRBC110 for SUA3000RM2U). |
| Battery Low | Runtime < 2 minutes at current load. | Shutdown servers immediately. |
| Overloaded – Reduce Load | Connected load exceeds UPS capacity. | Disconnect non-critical equipment; review load balance. |
| Bypass – Service Mode | UPS internal fault; utility passing directly to output. | Equipment is unprotected — contact APC support. |
| Charging – XX % | Battery is charging after a discharge event. | Normal; full charge may take 3–8 hours after a deep discharge. |
| Self-Test | Scheduled self-test in progress (runs weekly). | Normal; will complete in < 30 seconds. |

Audible Alarm Patterns

| Alarm Pattern | Meaning |
| --- | --- |
| 4 beeps every 30 seconds | Battery needs replacement — Replace Battery LED will also be lit. |
| Continuous beeping | Battery critically low — shutdown immediately. |
| 2 beeps every 30 seconds | On battery — utility power failure in progress. |
| Single long beep on startup | UPS powered on and self-test passed — normal. |

Preventive Maintenance Checklist

- Monthly: Verify Online LED is solid green and LCD shows "Online – Utility OK."

- Monthly: Check battery charge percentage via LCD or APC PowerChute software.

- Quarterly: Review self-test logs in PowerChute Business Edition.

- Annually: Inspect battery for swelling, leakage, or high internal temperature.

- Every 7–10 years: Replace batteries proactively per APC recommendation (APCRBC110).

Support Information

| Name | Role | Email | Phone |
| --- | --- | --- | --- |
| IT Helpdesk | General IT / Facilities Coordination | helpdesk@bluestar.com | 1-800-742-9300 |
| Nguyen, Kim | Data Center & Facilities Engineer | knguyen@bluestar.com | x9325 |
| APC by Schneider Electric Support | Vendor Hardware Support | www.apc.com/support | 1-800-800-4272 |

Related Articles

• KB003 – Cisco Meraki MR45/MR46 Access Point LED Guide

• KB006 – Submitting an IT Support Request via the Self-Service Portal

• APC Replacement Battery Kit: APCRBC110 (order via Procurement)